## G1
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 1
Serie Number | : 220 5424
Running Hours | : 19.457
Pre-stop condition | : OK
Out put kWh | : 20.759.588 KWh
System starter | Minimum Air Pressure is 25 bar
Keterangan :
1. Already done E 50
2. Already done service Generator by EL Prima
3. The condition of the radiator is crumbling

## G2
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 2
Serie Number | : 220 5494
Running Hours | : 26.413
Pre-stop condition | : OK
Out put kWh | : 19.467.332 KWh
System starter | : Minimum Air Pressure is 25 bar
Keterangan :
1. 02 November 2013 are doing E-50 when RH 26.413
2. it is already done valve clearen oleh PT GTI
3. Replacement CAC side B dan Cleaning Actuator Valve side A dan B
4. it is already done service Generator by EL Prima

## G3
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 3
Serie Number | : 220 5502
Running Hours | : 25.863
Pre-stop condition | : OK
Out put kWh | : 31.203.034 KWh
System starter | : Minimum Air Pressure is 25 bar
Keterangan :
1. 10 May 2013 are doing E-50 when RH 24.444
2. it is already done service Generator by EL Prima

## G4
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 4
Serie Number | : 220 5536
Running Hours | : 25.243
Pre-stop condition | : OK
Out put kWh | : 29.775.418 KWh
System starter | : Minimum Air Pressure is 25 bar
Keterangan :
1. 25 March 2013 have been done E-50 with RH 22.840
and finished in 19 April 2013
di laksanakan oleh PT EA
2. have to make replacement CAC side A dan B
3. the generator has been serviced by EL Prima

## G5
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 5
Serie Number | : 220 5781
Running Hours | : 19.662
Pre-stop condition | : OK
Out put kWh | : 22.574.757 KWh
System starter | : Minimum Air Pressure is 25 bar
Keterangan :
OK dan stand by
1. the generator has been serviced by EL Prima

## G6
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 6
Serie Number | : 220 5714
Running Hours | : 23.692
Pre-stop condition | : OK
Out put kWh | : 29.037.604 KWh
System starter | : Battery 4 x 12 V
Keterangan :
1. cleaning must be done CAC side A dan B
2. the generator has been serviced by EL Prima

## G7
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 7
Serie Number | : 220 5724
Running Hours | : 25.187
Pre-stop condition | Process E50
Out put kWh | : 29.550.949 KWh
System starter | : Battery 4 x 12 V
Keterangan :
1. have been done E50 by PT GTI
2. the generator has been serviced by EL Prima

## G8
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 8
Serie Number | : 220 5797
Running Hours | : 22.002
Pre-stop condition | Process E50
Out put kWh | : 25.905.025 KWh
System starter | : Battery 4 x 12 V
Keterangan :
1. has been done E50 by PT GTI
2. the generator has been serviced by EL Prima

## G9
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 9
Serie Number | : 220 6001
Running Hours | : 20.587
Pre-stop condition | Process E50
Out put kWh | : 23.787.110 KWh
System starter | : Minimum Air Pressure is 25 bar
Keterangan :
1. the generator has been serviced by EL Prima
2. has been done E50 by PT GTI

## G10
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 10
Serie Number | : 220 5982
Running Hours | : 10.094
Pre-stop condition | : Generator in repair
Out put kWh | : 22.064.842 KWh
System starter | :Minimum Air Pressure is 25 bar
Keterangan :
1. the generator has been serviced by EL Prima

## G11
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 11
Serie Number | : 220 5965
Running Hours | : 19.579
Pre-stop condition | : Process E50
Out put kWh | : 23.722.280 KWh
System starter | : Battery 4 x 12 V
Keterangan :
OK dan stand by
1. has been done E50 by PT GTI
2. the generator has been serviced by EL Prima

## G12
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 Juni 2020
Gas Engine No | : 12
Serie Number | : 220 5958
Running Hours | : 18.830
Pre-stop condition | : Process E50
Out put kWh | : 22.728.486
System starter | : Battery 4 x 12 V
Keterangan :
1. has been done E50 by PT GTI
2. the generator has been serviced by EL Prima

## G13
DATA STATUS GAS ENGINE PT. NAPALIMA
Tanggal 5 juni 2020
Gas Engine No | : 13
Serie Number | : 220 5594
Running Hours | : 6,570
Pre-stop condition | : Process E50+
Out put kWh | : 8,250,787 KWh
System starter | : Tekanan udara minimal 25 bar
Keterangan :
1. has been done E50+ by PT GTI
2. the generator has been serviced by EL Prima

## G14
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 juni 2020
Gas Engine No | : 14
Serie Number | : 220 5573
Running Hours | : 8,469
Pre-stop condition | : OK
Out put kWh | : 10,765,366 KWh
System starter | : Tekanan udara minimal 25 bar
Keterangan :
1. Sudah dilakukan service Generator Oleh EL Prima

## G15
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 juni 2020
Gas Engine No | : 15
Serie Number | : 220 5575
Running Hours | : 11,249
Pre-stop condition | : OK
Out put kWh | : 14,428,222 KWh
System starter | : Tekanan udara minimal 25 bar
Keterangan :
1. Sudah dilakukan service Generator Oleh EL Prima

## G16
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 juni 2020
Gas Engine No | : 16
Serie Number | : 220 5726
Running Hours | : 8,648
Pre-stop condition | : OK
Out put kWh | : 25,868 KWh ( KWh meter rusak )
System starter | : Battery 4 x 12 V
Keterangan :
1. Sudah dilakukan service Generator Oleh EL Prima

## G17
DATA STATUS GAS ENGINE KIM STAR
Tanggal 5 juni 2020
Gas Engine No | : 17
Serie Number | : 220 5727
Running Hours | : 8,547
Pre-stop condition | : Stop (motorice Gas Mixer in repair)
Out put kWh | : 3,750,669 KWh
System starter | : Battery 4 x 12 V
Keterangan :
1. Sudah dilakukan service Generator Oleh EL Prima

## Sheet1
Invoice No | Referensi | Custamer | Date of service | Scope of work | SR Number
SMSI-12-0099 | 105-SERV/FAK/V/XII | PT.Emily Megawatt | 18,05,12 | Broken potential Transformer | SRC-12-100
SMSI-12-0167 | 167-SERV/FAK/IX/XII | PT.Emily Megawatt | 15,06,09,12 | Change Prechamber sleeve #4Cylinder 2 | SRC-12-166
SMSI-12-0169 | 169-SERV/FAK/IX/XII | PT.Emily Megawatt | 21,09,12 | Prechamber leaking E#3 | SRC-12-168
|  | PT.Emily Megawatt | 21,26,09,12 | Trouble shooting E#5 ( Exhause temp. Hight ) | SR-12-0665
|  | PT.Emily Megawatt | 19,10,12 | Cooling water leakage from Pre. valve no.11 | SR-12-0758
|  | PT.Emily Megawatt | 12,17,10,12 | Throtle valve damage | SR-12-0751
|  | PT.Emily Megawatt | 25,10,12 | Prechamber leakage E#2 cyl. 15 | SR-12-0787
TOTAL
|  | PT.Emily Megawatt | 04,12,12 | Blow by oil leakage E#1 | SR-12-0873
|  | PT.Emily Megawatt | 04,12,12 | Blow by oil leakage E#2 | SR-12-0874
|  | PT.Emily Megawatt | 20,21,12,12 | Replace Prechamber sleeve E#5 | SR-12-0938
|  | PT.Emily Megawatt | 22,12,12 | Replace blow by filter E#2 | SR-13-0004
|  | PT.Emily Megawatt | 2012.12 | Replace blow by filter E#1 | SR-13-0005
|  | PT.Emily Megawatt | 11,01,13 | Inspection E#3 trip with Throtle Valve jammi | SR-13-0054
|  | PT.Emily Megawatt | 12,06,13 | inspect broken exhaust pipe line | SR-13-0480
TOTAL